## Slide 1
Headquartered in Tulsa, Oklahoma, TESCORP distributes, fabricates, and services its line of standardized and specialty compression systems stateside and internationally. The heart of our company is our innovative engineered products and service team, available seven days a week to support our customers.
TESCORP is a team of engineering and manufacturing experts, celebrating over 30 years as the leader in environmental and vapor recovery solutions, specialty compressors, customer service and parts.
Areas of expertise for the engineering veterans include both standard systems and engineered compression systems for environmental, oil, and gas as well as general industrial sectors.
TESCORP utilizes full state-of-the-art 3D CAD modeling & drafting for all designs.
TESCORP’s large fabrication facility utilizes Section VIII, Division I, ASME Code VIII welding capabilities.
TESCORP also maintains a fully equipped machine shop & repair / service center.

## Slide 2: What is instrument air?
Throughout industry, much of the production equipment is pneumatically driven or controlled. The air required to perform this function comes from the facilities or site air compression system. In some industry functions, the produced air quality from the air compressor system is sufficient in its raw form to accomplish the required operations. But in the case where the site environmental conditions warrant or the process components require a cleaner, dryer air supply then the produced air must be conditioned to meet these requirements. In the oil & gas industry or those facilities where process controls and sensitive pneumatic machinery are operated the air quality supplied must meet “Instrument Air Quality” standards.

## Slide 3: Instrument Air Quality Standards
Air Standards
Standard Air Temperature & Pressure (STP) is measured as:
  Pressure=14.7 Psia
  Temperature=68o F
  Relative Humidity=40%
ANSI has produced air quality standards for the industry that must be utilized as the minimum requirements for the design and application of an “Instrument Air” system.
  ANSI /ISA–7.0.0–1996 is the globally-recognized quality standard for instrument air as defined by the Instrument Society of America. Below, we’ll go through the Standard’s Four Elements of instrument air quality for use in pneumatic instruments.

## Slide 4: Instrument Air Quality Standards
Pressure Dew Point
  According to the ISA standard, the pressure dew point, when measured at the dryer outlet, should be at least 18° F below the minimum temperature where any part of the instrument air system is exposed.
    The pressure dew point is that pressure and temperature where free moisture can form at any specific pressure.
Particle Size
  A maximum particle size of 40-micrometer in the instrument air system is acceptable for most pneumatic devices. Additional filtration should be added for pneumatic devices requiring instrument air with less than 40-micrometer particle sizes. After any maintenance or modification to the air system, the maximum particle size in the instrument air system should be verified to be less than 40-micrometers.

## Slide 5: Instrument Air Quality Standards
Lubricant Content
  Oil content should be as close to zero as possible, and under no circumstances should lubricant content exceed 1 ppm w/w or v/v. Any lubricant in the compressed air system should be evaluated for compatibility with end-use pneumatic devices.
Contaminants
  Instrument air should be free of contaminants and hazardous gases. If contamination exists in the compressor intake areas, the intake should be moved to a different elevation or location where it is free from contaminants. Sources of contamination may include painting, chemical cleaning and/or engine exhaust.

## Slide 6: P& ID Drawing

## Slide 7: Compressor Solution
How much pressure is required?
How much air flow is required?
What is the air quality required?
What is the operating duty cycle?
There is no one compressor type that “Is the Best”. Each type of compression has an application where it is the better choice for the service based on the customers requirements.
TESCORP utilizes many types of compressors. TESCORP selects the compressor by their merits to best meet a specific compression requirement or site environment.
What is the first cost?
What is the total cost of ownership?
What special requirements does this application demand?
Design Criteria Questions:
Equipment Selection Criteria Questions:

## Slide 8: Compressor Solution
AIR COMPRESSOR SELECTION
There are many factors in determining the best compressor type for each application. The first is the flow requirement in pressure & volume. Many types of compressors are available for varying applications. A quick reference can be made for the initial selection per the following:
 | Pressure Range** | Capacity Range** | Air Quality | Duty Cycle | Initial cost | 5 Year Cost
Reciprocating* Lubricated | 0-500 psig 0-35 bar | 0-125 cfm 0-60 l/sec | Low | 50-75% | Low | Med High
Reciprocating* Oil-less | 0-150 psig 0-10 bar | 0-100 cfm 0-48 l/sec | High | 50-75% | Med | High
Rotary Screw Lubricated | 0-230 psig 0-16 bar | 5-3000 cfm 0-85 m3/min | Low | 100% | Med | Med Low
Rotary Screw Oil-free | 0-150 psig 0-10 bar | 50-3000 cfm 1-85 m3/min | High | 100% | High | Med
Centrifugal | 0-350 psig 0-24 bar | 250-20000 cfm 7-560 m3/min | High | 100% | High | Low
Printed from QUINCY COMPRESSOR

## Slide 9: Dryer Solutions
Air Purge Regeneration - a common regenerative dryer system where the wet tower is dried by diverting a small flow of the dry air from the active drying tower back through the saturated tower. This dry air adsorbs the moisture and expels it to the atmosphere.
The two (2) most common regenerative process are:
Heater Regeneration - another common regenerative dryer system where the wet tower is dried by a heater element that is incorporated in the towers. When in the regeneration mode, the heater element heats the tower to the point of boiling the entrained water to a vapor that is expelled from the wet tower into the atmosphere.

## Slide 10: Dryer Solutions
Both dryer types accomplish the required dew point reduction and add some inefficiencies to the Instrument Air Unit by either utilizing some of the systems horsepower or adding extra electrical power requirements to the system. The consideration for this regeneration cost must be applied to the initial sizing of the compressor unit.
Air Purge Regeneration:
  Air purge system is the simplest system to implement.
  The air flow requirement for regeneration is usually 15-20 percent of the total air flow.
Heater Regeneration:
  Does not utilize any of the compressor capacity.
  Requires excess electrical power for regeneration.

## Slide 11: Dryer Solutions
The image above illustrates that the moisture laden air is flowing through and being dried in the tower No. 1 while the tower No. 2 is being regenerated for use once the first tower is saturated.
The image above indicates a reversal of process where the tower No. 2 is drying the airflow and the tower No. 1 is in the regeneration mode

## Slide 12: Air Storage
In most systems, the air compressor is sized to exceed the site air flow requirements. It meets and exceeds this volume and is then allowed to unload or reduce its work load until the demand for more air is required. The excess air produced when in the demand mode is stored in the air receivers that are incorporated within the Instrument Air Unit. These storage vessels (Receivers) store the excess air at an elevated air pressure to allow the compressor to cycle down and the system to still continue to supply the required air flow to meet the site requirements. They also act as a pressure pulsation buffer to supply a more consistent air pressure with little variance.

## Slide 13: Air Storage
The storage volume of the receiver is based upon the vessel volume and the excessive amount of pressure that it is stored at above the required site pressure requirements. This volume is calculated as “flow time” available from the storage at the site required flow:
T= (v (P1 – P2))/C) Pa
Or, if a extra volume capacity is required for additional flow time, then the storage volume is calculated by:
V=(T*C*Pa )/(P1 –P2 )
T= time in minutes of flow V= volume of the air receiver in Ft3
P1 = upper pressure limits (Psia) P2 =lower pressure limits (Psia)
C=air consumption to site (Scfm) Pa =atmospheric pressure (Psia)
The Instrument Air Unit storage volume may vary to meet the design requirements by adding more storage volume or operating at a higher storage pressure. These are variables within the system that are made in the initial design phase. But, at any time, “Dry Air” storage may be added to the site air system as an ancillary component.

## Slide 14: Air Storage
TESCORP Standard’s incorporates (2) air storage vessels on all Instrument Air Units.
Wet Air Storage - This is the first step in the drying process to meet a required site pressure dew point. The air stream being generated by the compressor at the desired discharge pressure will be water saturated.
  A significant amount of the entrained water vapor in the air stream will be simply eliminated in the wet air receiver by allowing a period of time for retention.
  This produced water is then eliminated by a condensate trap & drain from the air flow.
  By reducing the amount of entrained water in the air stream to the air dryer assembly we increase its efficiency and lessens the work load.
  The storage of the air in the wet air receiver also acts to stabilize the pressure surges and create a more steady flow into the air dryer assembly.

## Slide 15: Air Storage
TESCORP Standard’s incorporates (2) air storage vessels on all Instrument Air Units.
Dry Air Storage- This is conditioned air that is at the required dew point for safe storage and use in the site environment. Additional storage of this conditioned air maybe added at any time.
  Reduces cycling of the compressor.
  Allows the site latitude to meet demands that may exceed the compressor unit’s capacity.
Note: There is a codicil to the added storage volume in that consideration must be given to the “compressor loading”. This may require the compressor to stay 100% continuously loaded for extended periods of time costing excess power costs or excessive operating temperatures.

## Slide 16: Air Storage
The amount of condensate (free water) that can be eliminated from the air flow in the wet air storage receiver can be calculated by: (Denver, CO. example)
  Pa=12.2 Psia Atmospheric pressure at 5,000 Ft. altitude
  Ta=70oF Ambient temperature
  RH=70% Relative humidity
  Saturation pressure of water @ 70oF=0.363 Psia (from steam tables)
  Saturation pressure @ 70% RH= 0.363 x 0.7= 0.25 Psia
  Vapor pressure of dry air= 12.2 – 0.25= 11.95 Psia
  Mole fraction of water vapor= 0.25/12.2= 0.021
  With a compressor capacity of 150 Scfm. The water condensed=1.075 Gallons/Hr. (25.8 Gallons/Day)
Note: Most of this condensed water is removed in the wet air storage vessel thus justifying its usage in the system as a necessary component for producing “Instrument Air” quality.

## Slide 17: Condensate Management
Oil/Water Separator- Condensed water from the wet air storage and the pre-filter into the dryer is a combination of mostly produced water with traces of oil that is a carry-over from the compressor oil separator. Although minute in the percentage of concentration, the presence of this condensate prohibits it from free discharge into the environment. Therefore, this produced water must be conditioned prior to discharge through the use of an Oil/Water separator that removes the oil from the effluent.
The "OSD" Oil/Water Separator removes the oil from the produced water allowing it to be freely discharged into the environment.